## Instructions
Calculation Tool for
Fuel Oil Combustion < 100 Million BTU/h
Version 3.1, Last Updated: Mar, 2014 JA, YS, & ZI
This page contains necessary instructions that will help you use this calculator to estimate the amount of priority substances and other chemicals that are manufactured, processed, otherwise used (MPO) and released during the operation of fuel oil-fired boilers with a maximum thermal input of less than 100 Million BTU/h
How to use this calculator: | 1. Click on the "Input-Output" Tab
2. Fill out the appropriate amounts in the yellow boxes
3. Scroll down to view the Output Summary
Input Summary: | 1. Select the type of fuel oil used during the reporting year
2. Enter the sulfur content of the fuel oil used during the reporting year
3. Enter the quantity of fuel oil used during the reporting year
4. Indicate whether the boilers onsite are equipped with low NOx (nitrogen oxides) burners
5. Select other types of emission control technology installed on the boilers
6. Enter the total combined maximum thermal input for all boilers operated during the reporting year
Output summary: | This table gives you the estimated quantity of ChemTRAC priority substances this process manufacture, processed otherwise used and released for the reporting year.
Other processes: | If your facility has other activities or sources that MPO or release priority substances (chemicals), then you need to calculate the amounts of chemicals for these activities as well. Please go to the ChemTRAC website for other calculators and more information.
Total MPO and Releases: | Once you have your estimates for activiti(es) or process(es), enter the amounts of MPO and release of each substance from each process into the "Calculation of Totals" calculator (available at www.toronto.ca/chemtrac) to determine if you need to report.
Before you start make sure you have: | - the type of fuel oil used during the reporting year - the sulfur content of the fuel oil used during the reporting year (as a percentage, consult the fuel oil MSDS or contact your supplier if you are not sure)
- the quantity of fuel oil used during the reporting year
- the type of emissions control equipment installed on the boiler
- the total combined maximum thermal input for all boilers operated during the reporting year (in BTU/h)
Note: some of these may not apply to your facility
Calculations
All Substances
Input-Output
Instructions
References
You are here

## Input-Output
Version 3.1, Last Updated: Mar, 2014 JA, YS, & ZI
• This page gathers information related to the fuel oil fired boiler at your facility and shows the estimated amounts of priority substances manufactured, processed, otherwise used (MPO) or released by boilers
• Please provide all the information requested in the yellow cells. If a section does not apply to your facility, leave it blank.
• To determine if you need to report, add the amounts shown in the Output Summary table to any other MPOs or releases from other processes or sources, if any, in your facility. Then you need to compare the total to the reporting thresholds.
• You may use the Calculation of Totals spreadsheet to calculate the totals.
Please complete the INPUT table below.
| Type of fuel oil burned: |  |  |  |  | Unit Conversion Table
| Sulphur content of fuel (refer to MSDS or call your supplier): |  | % |  |  | 1 | gallons (US) | = | 3.7854 | litres
| Quantity of fuel consumed: |  | Litres |  |  | 1 | gallons (Imp) | = | 4.5461 | litres
| Are you boilers equipped with low NOx (nitrogen oxides) burners? |  |  |  |  | 1 | cubic metres (m3) | = | 1000 | litres
Are your boilers equipped with emission controls?
| Aggregate thermal input rating of all boilers <100 million Btu/h. |  | Btu/h
OUTPUT SUMMARY (Only ChemTRAC priority substances)
| ChemTRAC Priority Substances | Quantity (kg/yr)
|  | Manufactured1 | Processed1 | Otherwise Used1 | Released to Air1
| Nitrogen Oxides (NOx) | 0 | 0 | 0 | 0
| Formaldehyde | 0 | 0 | 0 | 0
| Benzene | 0 | 0 | 0 | 0
| Lead, and its compounds | 0 | 0 | 0 | 0
| Manganese, and its compounds | 0 | 0 | 0 | 0
| Mercury, and its compounds | 0 | 0 | 0 | 0
| Nickel, and its compounds | 0 | 0 | 0 | 0
| Cadmium, and its compounds | 0 | 0 | 0 | 0
| Chromium (hexavalent), and its compounds | 0 | 0 | 0 | 0
| Chromium (non-hexavalent), and its compounds | 0 | 0 | 0 | 0
| Particulate Matter (PM2.5) | 0 | 0 | 0 | 0
| Total Volatile Compound (VOCs) | 0 | 0 | 0 | 0
| PAHs | 0 | 0 | 0 | 0
1 Definitions available on References tab.
Calculations
All Substances
Instructions
References
Input-Output
You are here

## All Substances
Summary of Calculations
Version 3.1, Last Updated: Mar, 2014 JA, YS, & ZI
This page provides a summary of the estimated quantities of all substances manufactured, processed, otherwise used (MPO) and/or released.
ChemTRAC Priority Substances | CAS # | Quantity (kg/yr)
|  | Manufactured | Processed | Otherwise Used | Released to Air
Nitrogen Oxides (NOx) | 11104-93-1 | 0 | 0 | 0 | 0
Formaldehyde | 50-00-0 | 0 | 0 | 0 | 0
Benzene | 71-42-3 | 0 | 0 | 0 | 0
Lead, and its compounds | n/a | 0 | 0 | 0 | 0
Manganese, and its compounds | n/a | 0 | 0 | 0 | 0
Mercury, and its compounds | n/a | 0 | 0 | 0 | 0
Nickel, and its compounds | n/a | 0 | 0 | 0 | 0
Cadmium, and its compounds | n/a | 0 | 0 | 0 | 0
Chromium (hexavalent), and its compounds | n/a | 0 | 0 | 0 | 0
Chromium (non-hexavalent), and its compounds | n/a | 0 | 0 | 0 | 0
Particulate Matter (PM2.5) | n/a | 0 | 0 | 0 | 0
Total Volatile Compound (VOCs) | n/a | 0 | 0 | 0 | 0
PAHs | n/a | 0 | 0 | 0 | 0
Other Substances
Sulphur dioxide | 7446-09-5 | 0 | 0 | 0 | 0
Sulphur trioxide | 7446-11-9 | 0 | 0 | 0 | 0
Nitrous Oxide | 10024-97-2 | 0 | 0 | 0 | 0
Ethylbenzene | 100-41-4 | 0 | 0 | 0 | 0
Toluene | 108-88-3 | 0 | 0 | 0 | 0
Anthracene | 120-12-7 | 0 | 0 | 0 | 0
Pyrene | 129-00-0 | 0 | 0 | 0 | 0
Benzo(g,h,i)perylene | 191-24-2 | 0 | 0 | 0 | 0
Indeno(1,2,3-cd)pyrene | 193-39-5 | 0 | 0 | 0 | 0
Benzo(b,k)fluoranthene | 205-99-2 | 0 | 0 | 0 | 0
Fluoranthene | 206-44-0 | 0 | 0 | 0 | 0
Acenaphtylene | 208-96-8 | 0 | 0 | 0 | 0
Chrysene | 218-01-9 | 0 | 0 | 0 | 0
Dibenzo(a,h)anthracene | 53-70-3 | 0 | 0 | 0 | 0
Benz(a)anthracene | 55-56-3 | 0 | 0 | 0 | 0
Carbon monoxide | 630-08-0 | 0 | 0 | 0 | 0
1,1,1-Trichloroethane | 71-55-6 | 0 | 0 | 0 | 0
Molybdenum | 7439-98-7 | 0 | 0 | 0 | 0
Antimony | 7440-36-0 | 0 | 0 | 0 | 0
Arsenic | 7440-38-2 | 0 | 0 | 0 | 0
Barium | 7440-39-3 | 0 | 0 | 0 | 0
Beryllium | 7440-41-7 | 0 | 0 | 0 | 0
Cobalt | 7440-48-4 | 0 | 0 | 0 | 0
Copper | 7440-50-8 | 0 | 0 | 0 | 0
Vanadium | 7440-62-2 | 0 | 0 | 0 | 0
Zinc | 7440-66-6 | 0 | 0 | 0 | 0
Methane | 74-82-8 | 0 | 0 | 0 | 0
Phosphorus | 7723-14-0 | 0 | 0 | 0 | 0
Selenium | 7782-49-2 | 0 | 0 | 0 | 0
Phenanthrene | 85-01-8 | 0 | 0 | 0 | 0
Fluorene | 86-73-7 | 0 | 0 | 0 | 0
Naphthalene | 91-20-3 | 0 | 0 | 0 | 0
o-Xylene | 95-47-6 | 0 | 0 | 0 | 0
Chloride | n/a | 0 | 0 | 0 | 0
Fluoride | n/a | 0 | 0 | 0 | 0
NMTOC | n/a | 0 | 0 | 0 | 0
PM | n/a | 0 | 0 | 0 | 0
PM10 | n/a | 0 | 0 | 0 | 0
POM | n/a | 0 | 0 | 0 | 0
TOC | n/a | 0 | 0 | 0 | 0
Calculations
All Substances
Instructions
References
You are here
Input-Output

## Calculations
Calculations
Version 3.1, Last Updated: Mar, 2014 JA, YS, & ZI
• This page provides detailed calculations based on the information provided in the Input table. It also provides sample calculations and an assessment of emission factor data quality.
• If you have site specific emission factors you may use them in the table below. If you choose to insert your own emission factor ensure that the units have been converted accordingly.
Fuel | Low NOx | Contaminant | CAS # | Emission Factor (lb/103 gal) | Emission Rate (kg/yr) | Data Quality
No. 6 | None | Sulphur dioxide | 7446-09-5 | 157 | 0 | A
|  | Sulphur trioxide | 7446-11-9 | 2 | 0 | A
|  | Nitrogen oxides (NOx) | 11104-93-1 | 55 | 0 | A
|  | Carbon monoxide | 630-08-0 | 5 | 0 | A
|  | PM | n/a | 9.19 | 0 | A
|  | TOC | n/a | 1.605 | 0 | A
|  | Methane | 74-82-8 | 1 | 0 | A
|  | Non Methane TOC (NMTOC) | n/a | 1.13 | 0 | A
|  | PM10 | n/a | 8.0304 | 0 | C
|  | Particulate Matter (PM2.5) | n/a | 5.2304 | 0 | C
|  | Nitrous Oxide | 10024-97-2 | 0.53 | 0 | E
|  | POM | n/a | 0.0013 | 0 | E
|  | Formaldehyde | 50-00-0 | 0.061 | 0 | E
|  | Benzene | 71-42-3 | 0.000214 | 0 | C
|  | Ethylbenzene | 100-41-4 | 6.36e-05 | 0 | E
|  | Naphthalene | 91-20-3 | 0.00113 | 0 | C
|  | 1,1,1-Trichloroethane | 71-55-6 | 0.000236 | 0 | E
|  | Toluene | 108-88-3 | 0.0062 | 0 | D
|  | o-Xylene | 95-47-6 | 0.000109 | 0 | E
|  | Acenaphthene | 83-32-9 | 2.11e-05 | 0 | C
|  | Acenaphtylene | 208-96-8 | 2.53e-07 | 0 | D
|  | Anthracene | 120-12-7 | 1.22e-06 | 0 | C
|  | Benz(a)anthracene | 55-56-3 | 4.01e-06 | 0 | C
|  | Benzo(b,k)fluoranthene | 205-99-2 | 1.48e-06 | 0 | C
|  | Benzo(g,h,i)perylene | 191-24-2 | 2.26e-06 | 0 | C
|  | Chrysene | 218-01-9 | 2.38e-06 | 0 | C
|  | Dibenzo(a,h)anthracene | 53-70-3 | 1.67e-06 | 0 | D
|  | Fluoranthene | 206-44-0 | 4.84e-06 | 0 | C
|  | Fluorene | 86-73-7 | 4.47e-06 | 0 | C
|  | Indeno(1,2,3-cd)pyrene | 193-39-5 | 2.14e-06 | 0 | C
|  | Phenanthrene | 85-01-8 | 1.05e-05 | 0 | C
|  | Pyrene | 129-00-0 | 4.25e-06 | 0 | C
|  | Antimony | 7440-36-0 | 0.00525 | 0 | E
|  | Arsenic | 7440-38-2 | 0.00132 | 0 | C
|  | Barium | 7440-39-3 | 0.00257 | 0 | D
|  | Beryllium | 7440-41-7 | 2.78e-05 | 0 | C
|  | Cadmium, and its compounds | n/a | 0.000398 | 0 | C
|  | Chloride | n/a | 0.347 | 0 | D
|  | Chromium (non-hexavalent), and its compounds | n/a | 0.000845 | 0 | C
|  | Chromium (hexavalent), and its compounds | n/a | 0.000248 | 0 | C
|  | Cobalt | 7440-48-4 | 0.00602 | 0 | D
|  | Copper | 7440-50-8 | 0.00176 | 0 | C
|  | Fluoride | n/a | 0.0373 | 0 | D
|  | Lead, and its compounds | n/a | 0.00151 | 0 | C
|  | Manganese, and its compounds | n/a | 0.003 | 0 | C
|  | Mercury, and its compounds | n/a | 0.000113 | 0 | C
|  | Molybdenum | 7439-98-7 | 0.000787 | 0 | D
|  | Nickel, and its compounds | n/a | 0.0845 | 0 | C
|  | Phosphorus | 7723-14-0 | 0.00946 | 0 | D
|  | Selenium | 7782-49-2 | 0.000683 | 0 | C
|  | Vanadium | 7440-62-2 | 0.0318 | 0 | D
|  | Zinc | 7440-66-6 | 0.0291 | 0 | D
No. 5 | None | Sulphur dioxide | 7446-09-5 | 157 | 0 | A
|  | Sulphur trioxide | 7446-11-9 | 2 | 0 | A
|  | Nitrogen oxides (NOx) | 11104-93-1 | 55 | 0 | A
|  | Carbon monoxide | 630-08-0 | 5 | 0 | A
|  | PM | n/a | 10 | 0 | B
|  | TOC | n/a | 1.605 | 0 | A
|  | Methane | 74-82-8 | 1 | 0 | A
|  | NMTOC | n/a | 1.13 | 0 | A
|  | PM10 | n/a | 8.604 | 0 | C
|  | Particulate Matter (PM2.5) | n/a | 5.604 | 0 | C
|  | Nitrous Oxide(1) | 10024-97-2 | 0.53 | 0 | E
|  | POM(1) | n/a | 0.0013 | 0 | E
|  | Formaldehyde(1) | 50-00-0 | 0.061 | 0 | E
|  | Benzene | 71-42-3 | 0.000214 | 0 | C
|  | Ethylbenzene | 100-41-4 | 6.36e-05 | 0 | E
|  | Naphthalene | 91-20-3 | 0.00113 | 0 | C
|  | 1,1,1-Trichloroethane | 71-55-6 | 0.000236 | 0 | E
|  | Toluene | 108-88-3 | 0.0062 | 0 | D
|  | o-Xylene | 95-47-6 | 0.000109 | 0 | E
|  | Acenaphthene | 83-32-9 | 2.11e-05 | 0 | C
|  | Acenaphtylene | 208-96-8 | 2.53e-07 | 0 | D
|  | Anthracene | 120-12-7 | 1.22e-06 | 0 | C
|  | Benz(a)anthracene | 55-56-3 | 4.01e-06 | 0 | C
|  | Benzo(b,k)fluoranthene | 205-99-2 | 1.48e-06 | 0 | C
|  | Benzo(g,h,i)perylene | 191-24-2 | 2.26e-06 | 0 | C
|  | Chrysene | 218-01-9 | 2.38e-06 | 0 | C
|  | Dibenzo(a,h)anthracene | 53-70-3 | 1.67e-06 | 0 | D
|  | Fluoranthene | 206-44-0 | 4.84e-06 | 0 | C
|  | Fluorene | 86-73-7 | 4.47e-06 | 0 | C
|  | Indeno(1,2,3-cd)pyrene | 193-39-5 | 2.14e-06 | 0 | C
|  | Phenanthrene | 85-01-8 | 1.05e-05 | 0 | C
|  | Pyrene | 129-00-0 | 4.25e-06 | 0 | C
|  | Antimony | 7440-36-0 | 0.00525 | 0 | E
|  | Arsenic | 7440-38-2 | 0.00132 | 0 | C
|  | Barium | 7440-39-3 | 0.00257 | 0 | D
|  | Beryllium | 7440-41-7 | 2.78e-05 | 0 | C
|  | Cadmium, and its compounds | n/a | 0.000398 | 0 | C
|  | Chloride | n/a | 0.347 | 0 | D
|  | Chromium (non-hexavalent), and its compounds | n/a | 0.000845 | 0 | C
|  | Chromium (hexavalent), and its compounds | n/a | 0.000248 | 0 | C
|  | Cobalt | 7440-48-4 | 0.00602 | 0 | D
|  | Copper | 7440-50-8 | 0.00176 | 0 | C
|  | Fluoride | n/a | 0.0373 | 0 | D
|  | Lead, and its compounds | n/a | 0.00151 | 0 | C
|  | Manganese, and its compounds | n/a | 0.003 | 0 | C
|  | Mercury, and its compounds | n/a | 0.000113 | 0 | C
|  | Molybdenum | 7439-98-7 | 0.000787 | 0 | D
|  | Nickel, and its compounds | n/a | 0.0845 | 0 | C
|  | Phosphorus | 7723-14-0 | 0.00946 | 0 | D
|  | Selenium | 7782-49-2 | 0.000683 | 0 | C
|  | Vanadium | 7440-62-2 | 0.0318 | 0 | D
|  | Zinc | 7440-66-6 | 0.0291 | 0 | D
No. 4 | None | Sulphur dioxide | 7446-09-5 | 150 | 0 | A
|  | Sulphur trioxide | 7446-11-9 | 2 | 0 | A
|  | Nitrogen oxides (NOx) | 11104-93-1 | 20 | 0 | A
|  | Carbon monoxide | 630-08-0 | 5 | 0 | A
|  | PM | n/a | 7 | 0 | B
|  | TOC | n/a | 0.556 | 0 | A
|  | Methane | 74-82-8 | 0.216 | 0 | A
|  | NMTOC | n/a | 0.34 | 0 | A
|  | PM10 | n/a | 6.0228 | 0 | C
|  | Particulate Matter (PM2.5) | n/a | 3.9228 | 0 | C
|  | Nitrous Oxide(1) | 10024-97-2 | 0.53 | 0 | E
|  | POM(1) | n/a | 0.0013 | 0 | E
|  | Formaldehyde(1) | 50-00-0 | 0.061 | 0 | E
|  | Benzene | 71-42-3 | 0.000214 | 0 | C
|  | Ethylbenzene | 100-41-4 | 6.36e-05 | 0 | E
|  | Naphthalene | 91-20-3 | 0.00113 | 0 | C
|  | 1,1,1-Trichloroethane | 71-55-6 | 0.000236 | 0 | E
|  | Toluene | 108-88-3 | 0.0062 | 0 | D
|  | o-Xylene | 95-47-6 | 0.000109 | 0 | E
|  | Acenaphthene | 83-32-9 | 2.11e-05 | 0 | C
|  | Acenaphtylene | 208-96-8 | 2.53e-07 | 0 | D
|  | Anthracene | 120-12-7 | 1.22e-06 | 0 | C
|  | Benz(a)anthracene | 55-56-3 | 4.01e-06 | 0 | C
|  | Benzo(b,k)fluoranthene | 205-99-2 | 1.48e-06 | 0 | C
|  | Benzo(g,h,i)perylene | 191-24-2 | 2.26e-06 | 0 | C
|  | Chrysene | 218-01-9 | 2.238e-06 | 0 | C
|  | Dibenzo(a,h)anthracene | 53-70-3 | 1.67e-06 | 0 | D
|  | Fluoranthene | 206-44-0 | 4.84e-06 | 0 | C
|  | Fluorene | 86-73-7 | 4.47e-06 | 0 | C
|  | Indeno(1,2,3-cd)pyrene | 193-39-5 | 2.14e-06 | 0 | C
|  | Phenanthrene | 85-01-8 | 1.05e-05 | 0 | C
|  | Pyrene | 129-00-0 | 4.25e-06 | 0 | C
|  | Antimony | 7440-36-0 | 0.00525 | 0 | E
|  | Arsenic | 7440-38-2 | 0.00132 | 0 | C
|  | Barium | 7440-39-3 | 0.00257 | 0 | D
|  | Beryllium | 7440-41-7 | 2.78e-05 | 0 | C
|  | Cadmium, and its compounds | 7440-43-9 | 0.000398 | 0 | C
|  | Chloride | n/a | 0.347 | 0 | D
|  | Chromium (non-hexavalent), and its compounds | n/a | 0.000845 | 0 | C
|  | Chromium (hexavalent), and its compounds | n/a | 0.000248 | 0 | C
|  | Cobalt | 7440-48-4 | 0.00602 | 0 | D
|  | Copper | 7440-50-8 | 0.00176 | 0 | C
|  | Fluoride | n/a | 0.0373 | 0 | D
|  | Lead, and its compounds | n/a | 0.00151 | 0 | C
|  | Manganese, and its compounds | n/a | 0.003 | 0 | C
|  | Mercury, and its compounds | n/a | 0.000113 | 0 | C
|  | Molybdenum | 7439-98-7 | 0.000787 | 0 | D
|  | Nickel, and its compounds | n/a | 0.0845 | 0 | C
|  | Phosphorus | 7723-14-0 | 0.00946 | 0 | D
|  | Selenium | 7782-49-2 | 0.000683 | 0 | C
|  | Vanadium | 7440-62-2 | 0.0318 | 0 | D
|  | Zinc | 7440-66-6 | 0.0291 | 0 | D
Distillate(2) | None | Sulphur dioxide | 7446-09-5 | 142 | 0 | A
|  | Sulphur trioxide | 7446-11-9 | 2 | 0 | A
|  | Nitrogen oxides (NOx) | 11104-93-1 | 20 | 0 | A
|  | Carbon monoxide | 630-08-0 | 5 | 0 | A
|  | PM | n/a | 2 | 0 | A
|  | TOC | n/a | 0.556 | 0 | A
|  | Methane | 74-82-8 | 0.216 | 0 | A
|  | NMTOC | n/a | 0.34 | 0 | A
|  | PM10 | n/a | 1 | 0 | C
|  | Particulate Matter (PM2.5) | n/a | 0.25 | 0 | C
|  | Nitrous Oxide | 10024-97-2 | 0.26 | 0 | E
|  | POM | n/a | 0.0033 | 0 | E
|  | Formaldehyde | 50-00-0 | 0.061 | 0 | E
Fuel |  | Contaminant | CAS# | Emission factor (lb/1012BTU) | Emission Rate (kg/yr) | Data Quality
Distillate |  | Cadmium, and its compounds | n/a | 3 | 0 | E
|  | Chromium (non-hexavalent), and its compounds | n/a | 3 | 0 | E
|  | Lead, and its compounds | n/a | 9 | 0 | E
|  | Mercury, and its compounds | n/a | 3 | 0 | E
|  | Manganese, and its compounds | n/a | 6 | 0 | E
|  | Nickel, and its compounds | n/a | 3 | 0 | E
n/a - not applicable
Note (1) - emission factors for nitrous oxide, POM, and formaldehyde are given for No. 6 fuel oil, and are assumed to be the same for No. 4 and No. 5 residual oils
Note (2) - distillate oil is No. 1 and No. 2 fuel oils
Sample Calculations:
For 1000 L of No. 6 Fuel Oil, with a sulphur content of 1%, consumed in a boiler with no emissions control equipment:
| Particulate Matter 2.5 (PM2.5) emission rate = | Quantity of fuel oil used (L/yr) X 0.264172 gal/L X Emission Factor (lb/103 gal) X 0.4536 kg/lb
| = | 1000 L/yr X 0.264172 gal/L X (8.03 X 1 +0.37) lb/103 gal X 0.4536 kg/lb
| PM2.5 emission rate = | 1.0066
Oil Type | 0 | Low NOx | Control | Efficiency
Select |  | Select | No | 0%
No. 1 Fuel Oil |  | Yes | Yes - electrostatic precipitator | 99.2%
No. 2 Fuel Oil |  | No | Yes - scrubber | 94%
No. 4 Fuel Oil |  | 3 | Yes - cyclone | 80%
No. 5 Fuel Oil |  |  | 1
No. 6 (Bunker C) Fuel Oil
1
Calculations
All Substances
Input-Output
Instructions
References
You are here

## References
References
Version 3.1, Last Updated: Mar, 2014 JA, YS, & ZI
This page provides all the reference information for the emission factors and assumptions used in the Calculations spreadsheet. Click on the links below to view the source documents.
Emission factors and an assessment of their data quality are provided in the US EPA AP-42 "Fuel Oil Combustion", Section 1.3, 1998
http:\www.epa.gov\ttn\chief\ap42\ch01\final\c01s03.pdf
Definitions1
Manufacture - To produce, prepare or compound a priority substance and includes the conincidental production of a priority.substance as a by-product.
Process - The preparation of a priority substance, after its manufacture, for commercial distribution and includes the preparation of a substance in the same physical state or chemical form as that received by the facility, or preparation which produces a change in physical state or chemical form.
Otherwise Use - Any use, disposal or release of a priority substance at a facility that does not fall under the definitions of "manufacture" or "process." This includes the use of the priority substance as a chemical processing aid, manufacturing aid or some other use.
Release - The emission or discharge of a priority substance, whether intentional, accidental or coincidental, from a facility into the environment.
1 For details refer to the Environmental Reporting and Disclosure Bylaw available at the ChemTRAC website.
Copyright (C) 2010, City of Toronto
This tool is provided solely as an aid, and the City of Toronto makes no representation or warranty as to its applicability to your facility or to your obligation to comply with the Environmental Reporting and Disclosure Bylaw (Municipal Code Chapter 423). It is the responsibility of each facility owner or operator to take the necessary steps to ensure compliance with the bylaw.
Calculations
All Substances
Instructions
References
You are here
Input-Output