DISINFECTION PROPOSAL PLAN

## Disinfection Criteria

|  |  |  |  |
| --- | --- | --- | --- |
| **Type of Installation:** | * **Watermain**
 | * **By-pass**
 | * **Service Hose**
 |
| **Pipe Diameter : mm** | Length: m | **Pipe Material: PVC, DI, Other:\_\_\_\_\_\_\_\_\_\_\_\_** |
| **Disinfection Method:** | * **Continuous Feed**
 | * **Slug**
 | **Concentration: mg/L** |
| **Contact Time:** | * **24 hrs**
 | * **3 hrs**
 |  |  |
| **Backflow Preventer to be used:**  | * **RP**
 |  | **Disinfectant to be used:** |
| **Discharge to:** | * **Storm**
* **Sanitary**
* **Combined**
 | **Location of source water:** |
| **Source provided by:** | * **Watermain Hydrant**
* **By-pass**
 |

|  |
| --- |
| **Disinfection Site Map:**Note: If this sketch area is not used with submission  **any attached sketch must include all pertinent information N** |

|  |
| --- |
| **Identify the following:** Line valves (V-1, V-2, V-3, etc.):CL2 Application (A)Flushing (F) example: F-1, F-2Sampling (S) example: S-1, S-2Backflow Preventer (BFP) |

|  |
| --- |
| **Contractor Company Name:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Date:****Contractor Representative Name*****Print:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Signature:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_*** |

|  |
| --- |
| **Approved by Contract Administrator Date:** ***Print:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Signature:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_*** |

**DISINFECTION RECORD**

#### Contract Administrator: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Contractor Company Name: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Drawing Attached: [ ]  Yes [ ]  No Disinfectant Used: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Disinfection of: [ ]  Watermain [ ]  By-pass [ ]  Service Hose Backflow Preventer Used: [ ]  RP

Complete All Items On This Disinfection Checklist:

* Backflow prevention device tested by certified tester and test form submitted
* Pipe hydrostatic pressure tested prior to disinfection
* Flushing / Scouring velocity met
* Disinfection Process documented (Complete Table 1)
* Water quality documented during bacteriological sampling (Complete Table 2)
* Post-flushing water quality criteria met: Turbidity is less than 1 NTU, Total Chlorine Residual is between 0.50 mg/L and 2.5 mg/L
* Submitted all laboratory bacteriological sample chain of custody / submission forms with this form

Table 1: Disinfection Process

|  |  |  |
| --- | --- | --- |
| Location ID | START | END |
| Date | Turbidity | Total Chlorine Residual | Total Chlorine Residual |
| NTU | Time of Testing | Initial (mg/L) | Time of Testing | After Contact Time (mg/L) | Date | Time of Testing |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |

The following people acknowledge that the above information conforms to the limits set out in TS 7.30~~:~~

Certified Operator/ Water Quality Analyst: [Print] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

[Signature] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ [OWWCO Certificate No.]\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Contract Administrator: [Print] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ [Signature] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

SAMPLING AND TESTING

1. Confirm that second set of bacteriological sampling is a minimum 16 hours after the first set: [ ]  Yes
2. Licensed Laboratory performing analysis: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Table 2A: Post-flushing Water Quality, Sampling and Testing Record (First of Two Consecutive Sets of Samples)

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Location ID and Bacteriological Sample Description | Date | Time of Sampling | \*Turbidity (NTU) | \*Total Chlorine Residual (mg/L) | Lab Chain of Custody / Sample Submission No. |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |

\*Turbidity and Total Chlorine Residual MUST be field-tested at the same time(s) and at the same location(s) as any bacteriological sampling

**Table 2B: Post-flushing Water Quality, Sampling and Testing Record (Second of Two Consecutive Sets of Samples)**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Location ID and Bacteriological Sample Description | Date | Time of Sampling | \*Turbidity (NTU) | \*Total Chlorine Residual (mg/L) | Lab Chain of Custody / Sample Submission No. |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |

\*Turbidity and Total Chlorine Residual MUST be field-tested at the same time(s) and at the same location(s) as any bacteriological sampling

The following people acknowledge that the above information conforms to the limits set out in TS 7.30~~:~~

Certified Operator / Water Quality Analyst: [Print] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

[Signature] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ [OWWCO Certificate NO.]\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Contract Administrator: [Print] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ [Signature] \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_